## Slide 1
Liquid level sensor/transmitter 24V AC or DC Liq. temp max 80°C Ambient temp -30-50°C | Oil | R744 CO2 R600 Butane R600a Isobutane R290 Propane | Synthetic refrigerants HFC/HFO/CFC | R717 NH3, Water, Alcohols | Dirty water In a metal vessel/tank
Rigid probe analog output only | HBLC-OIL 200-3000 mm | HBLC-CO2 200-3000 mm | HBLC-HFC 200-3000 mm | HBLT-A2 (max 50°C recommended) HBLT-A3 all temperatures 200-3000 mm | HBLC 200-2000 mm
Rigid probe analog and direct control output | HBSLC-OIL/C HBSLC-OIL/S HBSLC-OIL/PWM 200-3000 mm | HBSLC-CO2/C HBSLC-CO2/S HBSLC-CO2/PWM 200-3000 mm | HBSLC-HFC/C HBSLC-HFC/S HBSLC-HFC/PWM 200-3000 mm | HBSLT-A2/C HBSLT-A2/S HBSLT-A2/PWM 200-3000 mm | HBSLC/C HBSLC/S HBSLC/PWM 200-2000 mm
Wire/Flex probe analog output only | HBLT-FLEX 300-2000 mm | HBLT-FLEX 300-2000 mm | HBLT-W-Wire 600-6000 mm | HBLT-W-Wire 600-6000 mm | HBLT-W-Wire 600-6000 mm
Wire/Flex probe analog and direct control output | HBSLT-FLEX/C HBSLT-FLEX/S HBSLT-FLEX/PVM 300-2000 mm | HBSLT-FLEX/C HBSLT-FLEX/S HBSLT-FLEX/PVM 300-2000 mm | HBSLT-W-Wire/C HBSLT-W-Wire/S HBSLT-W-Wire/PWM 600-6000 mm | HBSLT-W-Wire/C HBSLT-W-Wire/S HBSLT-W-Wire/PWM 600-6000 mm | HBSLT-W-Wire/C HBSLT-W-Wire/S HBSLT-W-Wire/PWM 600-6000 mm
Low-cost probe analog output only | HBLC- thin 200-1600 mm | On request | HBLC- Fgas 200-1600 mm | HBLC 200-2000 mm | HBLC 200-2000 mm
Low-cost probe analog and direct control output | On request | On request | On request | HBLC/C HBLC/S HBLC/PWM 200-2000 mm | HBLC/C HBLC/S HBLC/PWM 200-2000 mm
Indicate the switch is available in an ATEX/IECEx version
1”
½”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
¾”
½”
1”
1”
½”
¾”
Connection diameter available
Level sensors/transmitters for different types of liquids

## Slide 2
Settings
All the sensors has numerous settings for making the measurement more accurate provide alarms etc.
The sensor can be connected to a PC with HB tool installed using an USB/M12 connection cable.
The tool can be downloaded for free from our web page.
Sensors with direct valve control and analog output
Sensors with an output cable can control a valve directly. Three different versions exist
/C for modulating valve
/S for stepper motor
/PWM for pulse modulating valve
24V versions
1: +24 VDC (Brown)
2: not used
3: not used
4: Analog output (Black)
5: not used
ATEX/IECEx approved sensors with IEC 61076-2-101 M12 plug
Most of the 24V sensors are available in an ATEX/IECEx approved version. The switch has a two-wire analog output which will grow linear to the level from 4 to 20 mA. The switch has settings which can be changed when connecting it to the HB-tool.
The sensor is used together with a barrier to comply with ATEX/IECEx requirements.
1: +24 VDC or 24VAC (Brown)
2: - common or 24VAC (White)
3: Remote input 4-20 mA (Blue)
4: Analog output 4-20 mA (Black)
5: Run-in signal (Grey)
Settings and Connections
Valve
Sensors with analog output
All sensors has an analog output
1: +24 VDC or 24VAC (Brown)
2: - common or 24VAC (White)
3: Remote input 4-20 mA (Blue)
4: Analog output 4-20 mA (Black)
5: Run-in signal (Grey)
Analog output
4 – 20 mA
Sensor with ISO 4400 connector
Sensor with M12 connector

## Slide 3
Product ordering codes and thread connections
Thread codes (stamped on the sensor )
1 = ½” NPT
2 = ¾” NPT
3 = ½” BSPT
4 = ¾” BSPT
5 = ½” BSPP
6 = ¾” BSPP
7 = 1 1/8” UNEF
8 = 1” BSPP
9 = 1” NPT
10 = 1 ¼” BSPP
11 = 1 ½” BSPP
12 = 1 ½” NPT
13 = ¼” BSPP
14 = ¼” NPT
15 = 3/8” NPT
16 = 1 ¼” UNF
NPT (National Pipe Taper)
BSPT (British Standard Pipe Taper (“R”))
BSPP (British Standard Pipe Parallel (“G”))
UNEF (Unified National Extra Fine)
UNF (Unified National Fine)
HBSLT/C-A2-30-6
Main product code
Cable output for modulating valve
Length
Thread
Other commonly used codes
U: union connection instead of V track with set screws (standard)
L: Long version
IP: ice proof (low temperature version)
LT: Low temperature version
MT: Medium temperature version
HT: High temperature version
HP: Heat pump version
HFC: suited for HFC,HFO,CFC and other synthetic refrigerants
/C: Built in controller for modulating valve
/S: Built in controller for stepper motor valve
/PWM: Built in controller for pulse width modulating valve
SSR-1: Solid state relay output for 24V DC/AC supply
SSR-2: Solid state relay output for 90-240 V AC supply